## System Limitations - DAPR
System Limitations DAPR
Substation/Feeder Name | Peak season | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longtitude | Location of constraint (end) Latitude | Location of constraint (end) Longtitude | Asset ID | Network Element | Residential customers affected | Residential customers affected (%) | Asset rating (MVA) S23/24 or W23 | Asset rating (MVA) S24/25 or W24 | Asset rating (MVA) S25/26 or W25 | Asset rating (MVA) S26/27 or W26 | Asset rating (MVA) S27/28 or W27 | Asset rating (MW) S23/24 or W23 | Asset rating (MW) S24/25 or W24 | Asset rating (MW) S25/26 or W25 | Asset rating (MW) S26/27 or W26 | Asset rating (MW) S27/28 or W27 | Forecast Demand POE50 (MVA) S23/24 or W23 | Forecast Demand POE50 (MVA) S24/25 or W24 | Forecast Demand POE50 (MVA) S25/26 or W25 | Forecast Demand POE50 (MVA) S26/27 or W26 | Forecast Demand POE50 (MVA) S27/28 or W27 | Forecast Demand POE10 (MVA) S23/24 or W23 | Forecast Demand POE10 (MVA) S24/25 or W24 | Forecast Demand POE10 (MVA) S25/26 or W25 | Forecast Demand POE10 (MVA) S26/27 or W26 | Forecast Demand POE10 (MVA) S27/28 or W27 | Forecast Demand POE50 (MW) S23/24 or W23 | Forecast Demand POE50 (MW) S24/25 or W24 | Forecast Demand POE50 (MW) S25/26 or W25 | Forecast Demand POE50 (MW) S26/27 or W26 | Forecast Demand POE50 (MW) S27/28 or W27 | Forecast Demand POE10 (MW) S23/24 or W23 | Forecast Demand POE10 (MW) S24/25 or W24 | Forecast Demand POE10 (MW) S25/26 or W25 | Forecast Demand POE10 (MW) S26/27 or W26 | Forecast Demand POE10 (MW) S27/28 or W27 | Voltage level | Maximum Load at risk (MW) S23/24 or W23 | Maximum Load at risk (MW) S24/25 or W24 | Maximum Load at risk (MW) S25/26 or W25 | Maximum Load at risk (MW) S26/27 or W26 | Maximum Load at risk (MW) S27/28 or W27 | Energy at risk (MWh) S23/24 or W23 | Energy at risk (MWh) S24/25 or W24 | Energy at risk (MWh) S25/26 or W25 | Energy at risk (MWh) S26/27 or W26 | Energy at risk (MWh) S27/28 or W27 | Preferred network investment | Preferred network investment capital cost ($M REAL) | Preferred network investment operating cost ($M REAL) | Preferred network investment cost accuracy (+ %) | Preferred network investment cost accuracy (- %) | Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Demand reduction required to defer investment by 1 year (MW) | Annual Deferral Value ($M) | Load transfer capability (MVA) | Load transfer capability (MW) | Emergency generation | Historic use of existing emergency resonponse | Project Index | Representative Interval Data | pf
Darlinghurst ZS | Summer | Asset condition - 11kV switchgear | -33.8782 | 151.2176 | -33.8782 | 151.2176 | ZN931 | Zone Substation | 8999 | 84.82% | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.3294 | 23.3294 | 23.3294 | 23.3294 | 23.3294 | 22.9059 | 22.4714 | 22.1709 | 22.0013 | 22.0828 | 25.0033 | 24.5268 | 24.2058 | 24.0362 | 24.1177 | 22.453 | 22.027 | 21.7325 | 21.5662 | 21.6461 | 24.5089 | 24.0419 | 23.7271 | 23.5609 | 23.6408 | 11kV | 0 | 0 | 0 | 0 | 0 | 2.531 | 3.5012 | 3.9458 | 4.7731 | 6.2546 | Transfer load to Campbell St 132/11kV zone and decommission Darlinghurst zone substation | 16.8 | 0.08 | 30% | 10% | 2028-03-01 | 3 | 2.9407 | 0.5587 | 15.3 | 14.9975 | NA | NA | 1 | Darlinghurst 33/11kV | 0.98023
Fdr 386 Surry Hills STS - Darlinghurst Tx 4 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8782 | 151.2176 | Fdr 386 | Sub-transmission line | 8999 | 84.82% | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 22.7 | 22.2 | 21.9 | 21.7 | 21.8 | NA | NA | NA | NA | NA | 22.2511 | 21.761 | 21.467 | 21.2709 | 21.3689 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Darlinghurst ZS |  |  |  |  | Transfer load to Campbell St 132/11kV zone and decommission Darlinghurst zone substation | [8 empty] | Combined with Darlinghurst ZS |  | NA | NA | 1 | Darlinghurst 33/11kV | 0.98023
Fdr 389 Surry Hills STS - Darlinghurst Tx 3 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8782 | 151.2176 | Fdr 389 | Sub-transmission line |  |  | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 22.7 | 22.2 | 21.9 | 21.7 | 21.8 | NA | NA | NA | NA | NA | 22.2511 | 21.761 | 21.467 | 21.2709 | 21.3689 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Darlinghurst ZS |  |  |  |  | Transfer load to Campbell St 132/11kV zone and decommission Darlinghurst zone substation | [8 empty] | Combined with Darlinghurst ZS |  | NA | NA | 1 | Darlinghurst 33/11kV | 0.98023
Milperra ZS | Winter | Asset condition - 11kV switchgear | -33.9381 | 150.9991 | -33.9381 | 150.9991 | ZN2196 | Zone Substation | 8207 | 85.1% | 64.6 | 64.6 | 64.6 | 64.6 | 64.6 | 62.9424 | 62.9424 | 62.9424 | 62.9424 | 62.9424 | 42.2 | 45.7 | 47.6 | 49 | 49.8 | 43.9 | 47.4 | 49.3 | 50.7 | 51.5 | 41.1172 | 44.5274 | 46.3786 | 47.7427 | 48.5222 | 42.7736 | 46.1837 | 48.035 | 49.3991 | 50.1785 | 11kV | 13.251 | 16.6612 | 18.5125 | 19.8765 | 20.656 | 5.08 | 5.83 | 6.51 | 7.17 | 7.77 | Replace 11kV compound switchgear at Milperra zone substation | 13 | 0.07 | 20% | 10% | 2025-12-01 | 12 | 11.6921 | 0.43233 | 28.6 | 27.8661 | NA | NA | 2 | Milperra 132/11kV | 0.97434
Pymble ZS | Winter | Asset condition - 11kV switchgear | -33.7487 | 151.1453 | -33.7487 | 151.1453 | ZN195 | Zone Substation | 8794 | 89.05% | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 40.5206 | 40.5206 | 40.5206 | 40.5206 | 40.5206 | 32.6 | 33.9 | 34.8 | 35.5 | 35.7 | 34.2 | 35.6 | 36.5 | 37.2 | 37.5 | 31.8306 | 33.0999 | 33.9787 | 34.6622 | 34.8574 | 33.3929 | 34.7598 | 35.6386 | 36.322 | 36.615 | 11kV | 2.9292 | 4.1985 | 5.0773 | 5.7608 | 5.956 | 5.54 | 6.04 | 6.52 | 7.08 | 7.59 | Replace 11kV compound switchgear at Pymble zone substation | 16 | 0.08 | 30% | 10% | 2027-09-01 | 4 | 3.9056 | 0.5321 | 29.6 | 28.9014 | NA | NA | 3 | Pymble 33/11kV | 0.9764
Fdr 9E1 Sydney East BSP - Kuringai STS | Winter | Asset Condition - 132kV feeder | -33.726 | 151.2083 | -33.7426 | 151.1564 | Fdr 9E1 | Sub-transmission line | 43989 | 93.88% | 286 | 286 | 286 | 286 | 286 | 257.4 | 257.4 | 257.4 | 257.4 | 257.4 | 149.8 | 153.4 | 155.1 | 155.8 | 156.3 | NA | NA | NA | NA | NA | 134.82 | 138.06 | 139.59 | 140.22 | 140.67 | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 8.46 | 9.03 | 9.58 | 10.21 | 10.87 | Replace 132kV feeders 9E1 and 9E2 oil filled UG sections | 10.4 | 0.05 | 20% | 10% | 2025-09-01 | 20 | 18 | 0.34586 | 0 | 0 | NA | NA | 4 | Kuringai 132/33kV | 0.9
Fdr 9E2 Sydney East BSP - Kuringai STS | Winter | Asset Condition - 132kV feeder | -33.726 | 151.2083 | -33.7426 | 151.1564 | Fdr 9E2 | Sub-transmission line |  |  | 286 | 286 | 286 | 286 | 286 | 257.4 | 257.4 | 257.4 | 257.4 | 257.4 | 149.6 | 153.1 | 154.9 | 155.6 | 156 | NA | NA | NA | NA | NA | 134.64 | 137.79 | 139.41 | 140.04 | 140.4 | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 9E1 Sydney East BSP - Kuringai STS |  |  |  |  | Replace 132kV feeders 9E1 and 9E2 oil filled UG sections | [8 empty] | 0 | 0 | NA | NA | 4 | Kuringai 132/33kV | 0.9
Fdr 769 Peakhurst STS - Blakehurst | Winter | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 769 | Sub-transmission line | 11628 | 94.63% | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 27.0087 | 27.0087 | 27.0087 | 27.0087 | 27.0087 | 25.2 | 26.1 | 26.7 | 27.7 | 27.5 | NA | NA | NA | NA | NA | 24.0502 | 24.9091 | 25.4817 | 26.4361 | 26.2452 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | 0.44 | 1.22 | 1.71 | 2.39 | 3.11 | Replace Fdr 769 & 770 with one 33kV feeder | 14.9 | 0.07 | 30% | 10% | 2026-03-01 | 3 | 2.8631 | 0.49551 | 11.2 | 10.689 | NA | NA | 5 | Blakehurst 33/11kV | 0.95437
Fdr 770 Peakhurst STS - Blakehurst | Winter | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 770 | Sub-transmission line |  |  | 28.3 | 28.3 | 28.3 | 28.3 | 28.3 | 27.0087 | 27.0087 | 27.0087 | 27.0087 | 27.0087 | 25.2 | 26.1 | 26.7 | 27.7 | 27.5 | NA | NA | NA | NA | NA | 24.0502 | 24.9091 | 25.4817 | 26.4361 | 26.2452 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 769 Peakhurst STS - Blakehurst |  |  |  |  | Replace Fdr 769 & 770 with one 33kV feeder | [8 empty] | 11.2 | 10.689 | NA | NA | 5 | Blakehurst 33/11kV | 0.95437
Willoughby STS | Summer | Asset Condition - 33kV switchgear | -33.8171 | 151.1855 | -33.8171 | 151.1855 | TS7220 | Sub-transmission Substation | 23746 | 87.56% | 225.4 | 225.4 | 225.4 | 225.4 | 225.4 | 224.5076 | 224.5076 | 224.5076 | 224.5076 | 224.5076 | 135.1 | 138.3 | 148.7 | 164.7 | 179.7 | 144.2 | 147.4 | 157.7 | 173.8 | 188.7 | 134.5651 | 137.7524 | 148.1113 | 164.0479 | 178.9885 | 143.6291 | 146.8164 | 157.0756 | 173.1119 | 187.9529 | 33kV | 0 | 0 | 0 | 0 | 0 | 4.2 | 5.3 | 7 | 6 | 8.4 | Replacement of 33kV switchgear at Willoughby STS | 23.1 | 0.12 | 30% | 10% | 2027-09-01 | NA | NA | 0.76821 | 17.5 | 17.4307 | NA | NA | 6 | Willoughby 132/33kV | 0.99604
Merewether STS | Summer | Asset Condition - 33kV switchgear | -32.9351 | 151.7365 | -32.9351 | 151.7365 | TS00405 | Sub-transmission Substation | 47596 | 88.53% | 274.4 | 274.4 | 274.4 | 274.4 | 274.4 | 266.168 | 266.168 | 266.168 | 266.168 | 266.168 | 156.038 | 154.5723 | 153.3148 | 152.1908 | 151.5514 | 181.6749 | 180.0752 | 178.7469 | 177.6147 | 176.9706 | 151.3569 | 149.9351 | 148.7154 | 147.6251 | 147.0049 | 176.2247 | 174.6729 | 173.3845 | 172.2863 | 171.6615 | 33kV | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.63 | 0.65 | 0.66 | 0.67 | Replacement of 33kV switchgear at Merewether STS | [5 empty] | NA | NA | 0 | 30.2 | 29.294 | NA | NA |  | Merewether 13233kV | 0.97

## System Limitations TAPR - Lines
System Limitations TAPR - Lines
Transmission line ID | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longitude | Location of constraint (end) Latitude | Location of constraint (end) Longitude | Asset rating (MVA) S23/24 or W24 | Asset rating (MVA) S24/25 or W25 | Asset rating (MVA) S25/26 or W26 | Asset rating (MVA) S26/27 or W27 | Asset rating (MVA) S27/28 or W28 | Asset rating (MVA) S28/29 or W29 | Asset rating (MVA) S29/30 or W30 | Asset rating (MVA) S30/31 or W31 | Asset rating (MVA) S31/32 or W32 | Asset rating (MVA) S32/33 or W33 | Forecast Demand P50 (MVA) S23/24 or W24 | Forecast Demand P50 (MVA) S24/25 or W25 | Forecast Demand P50 (MVA) S25/26 or W26 | Forecast Demand P50 (MVA) S26/27 or W27 | Forecast Demand P50 (MVA) S27/28 or W28 | Forecast Demand P50 (MVA) S28/29 or W29 | Forecast Demand P50 (MVA) S29/30 or W30 | Forecast Demand P50 (MVA) S30/31 or W31 | Forecast Demand P50 (MVA) S31/32 or W32 | Forecast Demand P50 (MVA) S32/33 or W33 | Forecast Demand P10 (MVA) S23/24 or W24 | Forecast Demand P10 (MVA) S24/25 or W25 | Forecast Demand P10 (MVA) S25/26 or W26 | Forecast Demand P10 (MVA) S26/27 or W27 | Forecast Demand P10 (MVA) S27/28 or W28 | Forecast Demand P10 (MVA) S28/29 or W29 | Forecast Demand P10 (MVA) S29/30 or W30 | Forecast Demand P10 (MVA) S30/31 or W31 | Forecast Demand P10 (MVA) S31/32 or W32 | Forecast Demand P10 (MVA) S32/33 or W33 | Voltage level | Maximum Load at risk per year (MVA)* S23/24 or W24 | Maximum Load at risk per year (MVA)* S24/25 or W25 | Maximum Load at risk per year (MVA)* S25/26 or W26 | Maximum Load at risk per year (MVA)* S26/27 or W27 | Maximum Load at risk per year (MVA)* S27/28 or W28 | Maximum Load at risk per year (MVA)* S28/29 or W29 | Maximum Load at risk per year (MVA)* S29/30 or W30 | Maximum Load at risk per year (MVA)* S30/31 or W31 | Maximum Load at risk per year (MVA)* S31/32 or W32 | Maximum Load at risk per year (MVA)* S32/33 or W33 | Maximum Load at risk per year (MW)* S23/24 or W24 | Maximum Load at risk per year (MW)* S24/25 or W25 | Maximum Load at risk per year (MW)* S25/26 or W26 | Maximum Load at risk per year (MW)* S26/27 or W27 | Maximum Load at risk per year (MW)* S27/28 or W28 | Maximum Load at risk per year (MW)* S28/29 or W29 | Maximum Load at risk per year (MW)* S29/30 or W30 | Maximum Load at risk per year (MW)* S30/31 or W31 | Maximum Load at risk per year (MW)* S31/32 or W32 | Maximum Load at risk per year (MW)* S32/33 or W33 | Energy at risk (MWh) S23/24 or W24 | Energy at risk (MWh) S24/25 or W25 | Energy at risk (MWh) S25/26 or W26 | Energy at risk (MWh) S26/27 or W27 | Energy at risk (MWh) S27/28 or W28 | Energy at risk (MWh) S28/29 or W29 | Energy at risk (MWh) S29/30 or W30 | Energy at risk (MWh) S30/31 or W31 | Energy at risk (MWh) S31/32 or W32 | Energy at risk (MWh) S32/33 or W33 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Historic line rating (MVA) S20/21 or W21 | Historic line rating (MVA) S21/22 or W22 | Historic line rating (MVA) S22/23 or W23 | Annual economic cost of constraint ($constant) S23/24 or W24 | Annual economic cost of constraint ($constant) S24/25 or W25 | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | VCR ($/MWh) | Annual costraint duration (hours)# | Constraint duration on peak demand day (hours)# | Project Index for interval data
Fdr 91A - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 58.8634 | 65.0112 | 53.9 | 62.4 | 67.8 | 58.7 | 57.7 | 55.7 | 58.4 | 58.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | 20.3 | 0.1 | 30% | 2029-09-01 | NA | 0.93217 | 97.17 | 97.17 | 97.17 | 4474650.6062 | 4823735.2552 | 5201459.7473 | 5610660.6611 | 6053347.7233 | 6532982.43 | 7049142.2518 | 7605376.945 | 8204073.4792 | 8849546.7988 | 46025 | 0 | 0 | 1
Fdr 91B - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 59.3001 | 65.5039 | 54.2 | 62.9 | 68.4 | 59 | 58.1 | 56.2 | 59 | 59 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | [6 empty] | 97.17 | 97.17 | 97.17 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 1
Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 68.645 | 75.3664 | 63.7 | 72.2 | 78.2 | 68.4 | 68.2 | 66.5 | 69.4 | 70.2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91X/1 | 1.03 | 0.01 | 30% | 2028-09-01 |  |  | 99.45 | 99.45 | 99.45 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 2
Fdr 91Y/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 87.4961 | 92.9428 | 86.9 | 90.8 | 97.7 | 89.6 | 89.8 | 89.4 | 92.7 | 95.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91Y/1 | [6 empty] | 99.45 | 99.45 | 99.45 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 2
Fdr 91X/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 68.4802 | 75.2445 | 63.5 | 72 | 78.1 | 68.3 | 68.1 | 66.4 | 69.3 | 70 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Install new 132kV series reactors to allow retirement of all four oil cables from Chullora STSS | 3.2 | 0 | 30% | 2028-09-01 |  |  | 100.6 | 100.6 | 100.6 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 3
Fdr 91Y/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 87.5389 | 92.9917 | 86.9 | 90.8 | 97.7 | 89.6 | 89.9 | 89.4 | 92.7 | 95.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Install new 132kV series reactors to allow retirement of all four oil cables from Chullora STSS | [6 empty] | 100.6 | 100.6 | 100.6 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 3
Fdr 92C - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 84.7015 | 90.3651 | 82.6 | 88 | 94.5 | 86.4 | 86.8 | 86.2 | 89.4 | 91.4 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Install new 132kV series reactors to allow retirement of all four oil cables from Chullora STSS | 3.5 | 0 | 30% | 2028-09-01 |  |  | 104.03 | 104.03 | 104.03 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 4
Fdr 92X - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 85.3874 | 90.9927 | 83 | 88.6 | 95.2 | 87.1 | 87.4 | 86.9 | 90.1 | 92.2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Install new 132kV series reactors to allow retirement of all four oil cables from Chullora STSS | [6 empty] | 104.03 | 104.03 | 104.03 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 4
*Maximum load at risk is provided for credible contingencies and only assumes committed projects
#Constraint duration provided for year of proposed timing of preferred investment

## System Limitations TAPR - STS
System Limitations TAPR - STS
Connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point (Latitude) | Constrained connection point (Longitude) | Annual energy of residential customers affected (MWh) | Peak demand of residential customers affected (MW) | Annual energy of industrial customers affected (MWh) | Peak demand of industrial customers affected (MW) | Annual energy of commercial customers affected (MWh) | Peak demand of commercial customers affected (MW) | Forecast P50 Max Demand on max demand day (MVA) & S23/24 or W24 | Forecast P50 Max Demand on max demand day (MVA) & S24/25 or W25 | Forecast P50 Max Demand on max demand day (MVA) & S25/26 or W26 | Forecast P50 Max Demand on max demand day (MVA) & S26/27 or W27 | Forecast P50 Max Demand on max demand day (MVA) & S27/28 or W28 | Forecast P50 Max Demand on max demand day (MVA) & S28/29 or W29 | Forecast P50 Max Demand on max demand day (MVA) & S29/30 or W30 | Forecast P50 Max Demand on max demand day (MVA) & S30/31 or W31 | Forecast P50 Max Demand on max demand day (MVA) & S31/32 or W32 | Forecast P50 Max Demand on max demand day (MVA)& S32/33 or W33 | Forecast P10 Max Demand on max demand day (MVA) S23/24 or W24 | Forecast P10 Max Demand on max demand day (MVA) S24/25 or W25 | Forecast P10 Max Demand on max demand day (MVA) S25/26 or W26 | Forecast P10 Max Demand on max demand day (MVA) S26/27 or W27 | Forecast P10 Max Demand on max demand day (MVA) S27/28 or W28 | Forecast P10 Max Demand on max demand day (MVA) S28/29 or W29 | Forecast P10 Max Demand on max demand day (MVA) S29/30 or W30 | Forecast P10 Max Demand on max demand day (MVA) S30/31 or W31 | Forecast P10 Max Demand on max demand day (MVA) S31/32 or W32 | Forecast P10 Max Demand on max demand day (MVA) S32/33 or W33 | Forecast P50 Max Demand on min demand day (MW) S23/24 or W24 | Forecast P50 Max Demand on min demand day (MW) S24/25 or W25 | Forecast P50 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P50 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P50 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P50 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P50 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P50 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P50 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P50 Max Demand on min demand day (MW) S32/33 or W33 | Forecast P10 Max Demand on min demand day (MW) S23/24 or W24 | Forecast P10 Max Demand on min demand day (MW) S24/25 or W25 | Forecast P10 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P10 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P10 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P10 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P10 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P10 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P10 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P10 Max Demand on min demand day (MW) S32/33 or W33 | Voltage level (kV) | Maximum Load at risk per year (MVA) S23/24 or W24 | Maximum Load at risk per year (MVA) S24/25 or W25 | Maximum Load at risk per year (MVA) S25/26 or W26 | Maximum Load at risk per year (MVA) S26/27 or W27 | Maximum Load at risk per year (MVA) S27/28 or W28 | Maximum Load at risk per year (MVA) S28/29 or W29 | Maximum Load at risk per year (MVA) S29/30 or W30 | Maximum Load at risk per year (MVA) S30/31 or W31 | Maximum Load at risk per year (MVA) S31/32 or W32 | Maximum Load at risk per year (MVA) S32/33 or W33 | Maximum Load at risk per year (MW) S23/24 or W24 | Maximum Load at risk per year (MW) S24/25 or W25 | Maximum Load at risk per year (MW) S25/26 or W26 | Maximum Load at risk per year (MW) S26/27 or W27 | Maximum Load at risk per year (MW) S27/28 or W28 | Maximum Load at risk per year (MW) S28/29 or W29 | Maximum Load at risk per year (MW) S29/30 or W30 | Maximum Load at risk per year (MW) S30/31 or W31 | Maximum Load at risk per year (MW) S31/32 or W32 | Maximum Load at risk per year (MW) S32/33 or W33 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Load transfer capacity (MVA) | Historic connection point rating (MVA) S20/21 or W21 | Historic connection point rating (MVA) S21/22 or W22 | Historic connection point rating (MVA) S22/23 or W23 | Limitation asset | Unplanned outages | Maximum fault level (MVA) | Annual economic cost of constraint ($constant) S23/24 or W24 | Annual economic cost of constraint ($constant) S24/25 or W25 | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | VCR ($/MWh) | Annual EUE (MWh) S23/24 or W24 | Annual EUE (MWh) S24/25 or W25 | Annual EUE (MWh) S25/26 or W26 | Annual EUE (MWh) S26/27 or W27 | Annual EUE (MWh) S27/28 or W28 | Annual EUE (MWh) S28/29 or W29 | Annual EUE (MWh) S29/30 or W30 | Annual EUE (MWh) S30/31 or W31 | Annual EUE (MWh) S31/32 or W32 | Annual EUE (MWh) S32/33 or W33 | Project Index for additional data%
Macquarie STS^ | Load growth - Substation capacity | Augmentation | -33.7872 | 151.1323 | N/A | N/A | N/A | N/A | N/A | N/A | 49.476 | 117.6 | 136.92 | 149.52 | 163.8 | 178.92 | 189 | 193.2 | 197.4 | 201.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 132 | 0 | 0 | 0 | 6.62 | 20.9 | 36.02 | 46.1 | 50.3 | 54.5 | 58.7 | 0 | 0 | 0 | 6.4876 | 20.482 | 35.2996 | 45.178 | 49.294 | 53.41 | 57.526 | Install 3rd 132/33kV transformer | 8.1 | 0.039 | 30% | 2025-12-31 | NA | 0.26937 | 0 | 0 | 142.89 | 142.89 | Transformer | N/A | 3596.361 | 2.4497 | 6.4102 | 13.5116 | 1882.8692 | 165520.1209 | 534892.8573 | 888979.1915 | 1148949.3711 | 1447534.191 | 1786014.7436 | 46025 | 5.3224e-05 | 0.00013928 | 0.00029357 | 0.04091 | 3.5963 | 11.6218 | 19.3151 | 24.9636 | 31.451 | 38.8053 | 5
Wallumatta STS (Macquarie Park) | Load growth - Substation capacity and connection points |  | -33.7872 | 151.1323 | N/A | N/A | N/A | N/A | N/A | N/A | 49.476 | 117.6 | 136.92 | 149.52 | 163.8 | 208.92 | 234 | 253.2 | 272.4 | 291.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 132 | 0 | 0 | 0 | 0 | 0 | 30 | 45 | 60 | 75 | 90 | 0 | 0 | 0 | 0 | 0 | 29.4 | 44.1 | 58.8 | 73.5 | 88.2 | Establish New Wallumatta STS |  |  |  | 2028-12-01 | NA | 0 | 0 | 0 | 0 | 0 | Transformer and 33kV switchgear | N/A |  | 0 | 0 | 0 | 0 | 0 | 6652453500 | 12155846850 | 16207795800 | 20259744750 | 24311693700 | 46025 | 0 | 0 | 0 | 0 | 0 | 144540 | 264114 | 352152 | 440190 | 528228