## System Limitations DAPR
System Limitations DAPR
Substation/Feeder Name | Peak season | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longtitude | Location of constraint (end) Latitude | Location of constraint (end) Longtitude | Asset ID | Network Element | Residential customers affected | Residential customers affected (%) | Asset rating (MVA) S24/25 or W24 | Asset rating (MVA) S25/26 or W25 | Asset rating (MVA) S26/27 or W26 | Asset rating (MVA) S27/28 or W27 | Asset rating (MVA) S28/29 or W28 | Asset rating (MW) S24/25 or W24 | Asset rating (MW) S25/26 or W25 | Asset rating (MW) S26/27 or W26 | Asset rating (MW) S27/28 or W27 | Asset rating (MW) S28/29 or W28 | Forecast Demand POE50 (MVA) S24/25 or W24 | Forecast Demand POE50 (MVA) S25/26 or W25 | Forecast Demand POE50 (MVA) S26/27 or W26 | Forecast Demand POE50 (MVA) S27/28 or W27 | Forecast Demand POE50 (MVA) S28/29 or W28 | Forecast Demand POE10 (MVA) S24/25 or W24 | Forecast Demand POE10 (MVA) S25/26 or W25 | Forecast Demand POE10 (MVA) S26/27 or W26 | Forecast Demand POE10 (MVA) S27/28 or W27 | Forecast Demand POE10 (MVA) S28/29 or W28 | Forecast Demand POE50 (MW) S24/25 or W24 | Forecast Demand POE50 (MW) S25/26 or W25 | Forecast Demand POE50 (MW) S26/27 or W26 | Forecast Demand POE50 (MW) S27/28 or W27 | Forecast Demand POE50 (MW) S28/29 or W28 | Forecast Demand POE10 (MW) S24/25 or W24 | Forecast Demand POE10 (MW) S25/26 or W25 | Forecast Demand POE10 (MW) S26/27 or W26 | Forecast Demand POE10 (MW) S27/28 or W27 | Forecast Demand POE10 (MW) S28/29 or W28 | Voltage level | Maximum Load at risk (MW) S24/25 or W24 | Maximum Load at risk (MW) S25/26 or W25 | Maximum Load at risk (MW) S26/27 or W26 | Maximum Load at risk (MW) S27/28 or W27 | Maximum Load at risk (MW) S28/29 or W28 | Energy at risk (MWh) S24/25 or W24 | Energy at risk (MWh) S25/26 or W25 | Energy at risk (MWh) S26/27 or W26 | Energy at risk (MWh) S27/28 or W27 | Energy at risk (MWh) S28/29 or W28 | Preferred network investment | Preferred network investment capital cost ($M REAL) | Preferred network investment operating cost ($M REAL) | Preferred network investment cost accuracy (+ %) | Preferred network investment cost accuracy (- %) | Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Demand reduction required to defer investment by 1 year (MW) | Annual Deferral Value ($M) | Load transfer capability (MVA) | Load transfer capability (MW) | Emergency generation | Historic use of existing emergency resonponse | Project Index | Representative Interval Data | pf
Fdr 386 Surry Hills STS - Darlinghurst Tx 4 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8781 | 151.2176 | Fdr 386 | Sub-transmission line | 7879 | 84.82% | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.8632 | 26.1383 | 25.6483 | 25.5812 | 25.6541 | NA | NA | NA | NA | NA | 26.332 | 25.6215 | 25.1411 | 25.0753 | 25.1468 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | 2.3745 | 3.0078 | 3.8758 | 5.2083 | 7.0967 | Replace 33kV gas feeders 386 and 389 | 7.7 | 0.0385 | 30% | 10% | 2027-09-01 | 2 | 1.9605 | 0.26326 | 15.2622 | 14.9604 | NA | NA | 2 | Darlinghurst 33/11kV | 0.98023
Fdr 389 Surry Hills STS - Darlinghurst Tx 3 | Summer | Asset condition - 33kV feeder | -33.8825 | 151.2122 | -33.8781 | 151.2176 | Fdr 389 | Sub-transmission line |  |  | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.5641 | 26.8957 | 26.168 | 25.677 | 25.6096 | 25.6799 | NA | NA | NA | NA | NA | 26.3639 | 25.6505 | 25.1693 | 25.1032 | 25.1721 | NA | NA | NA | NA | NA | 33kV | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 386 Surry Hills STS - Darlinghurst Tx4 |  |  |  |  | Replace 33kV gas feeders 386 and 389 |  |  | 30% | 10% |  |  |  |  | Combined with Fdr 386 Surry Hills STS - Darlinghurst Tx4 |  | NA | NA | 2 | Darlinghurst 33/11kV | 0.98023
Botany ZS | Summer | Asset condition - 11kV switchgear | -33.9476 | 151.2045 | -33.9476 | 151.2045 | ZN340 | Zone Substation | 7561 | 85% | 33 | 33 | 33 | 33 | 33 | 32.518 | 32.518 | 32.518 | 32.518 | 32.518 | 27.9658 | 27.7496 | 27.5021 | 27.6359 | 27.9279 | 30.6254 | 30.4003 | 30.1484 | 30.2822 | 30.5742 | 27.5573 | 27.3443 | 27.1004 | 27.2323 | 27.52 | 30.1781 | 29.9563 | 29.7081 | 29.8399 | 30.1277 | 11kV | 0 | 0 | 0 | 0 | 0 | 2.3517 | 2.4703 | 2.5935 | 2.7626 | 2.9612 | Replace 11kV compound switchgear at Botany zone substation | 9 | 0.045 | 30% | 10% | 2028-12-01 | 6 | 5.9124 | 0.30771 | 7.1916 | 7.0866 | NA | NA | 3 | Botany 33/11kV | 0.98539
Willoughby STS | Summer | Asset Condition - 33kV switchgear | -33.8171 | 151.1855 | -33.8171 | 151.1855 | TS7220 | Sub-transmission Substation | 24733 | 87.56% | 225.4 | 225.4 | 225.4 | 225.4 | 225.4 | 225.2249 | 225.2249 | 225.2249 | 225.2249 | 225.2249 | 129.7149 | 148.613 | 167.8768 | 178.5146 | 194.3391 | 135.3819 | 154.1667 | 173.3659 | 183.9986 | 199.816 | 129.6141 | 148.4975 | 167.7464 | 178.3759 | 194.1881 | 135.2767 | 154.0469 | 173.2312 | 183.8556 | 199.6607 | 33kV | 0 | 0 | 0 | 0 | 0 | 5.3252 | 7.0289 | 6.0452 | 8.3608 | 11.0075 | Replacement of 33kV switchgear at Willoughby STS | 42.5 | 0.2125 | 30% | 10% | 2029-09-01 | NA | NA | 1.4531 | 17.5 | 17.4864 | NA | NA | 4 | Willoughby 132/33kV | 0.99922
Merewether STS | Summer | Asset Condition - 33kV switchgear | -32.9351 | 151.7365 | -32.9351 | 151.7365 | TS00405 | Sub-transmission Substation | 47995 | 88.53% | 274.4 | 274.4 | 274.4 | 274.4 | 274.4 | 266.168 | 266.168 | 266.168 | 266.168 | 266.168 | 141.9 | 140.9 | 140.7 | 142.1 | 144.2 | 163.3 | 162.1 | 161.1 | 160.8 | 162.2 | 137.643 | 136.673 | 136.479 | 137.837 | 139.874 | 158.401 | 157.237 | 156.267 | 155.976 | 157.334 | 33kV | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.63 | 0.65 | 0.66 | 0.67 | Replacement of 33kV switchgear at Merewether STS | 28.9 | 0.1445 | 30% | 10% | 2029-09-01 | NA | NA | 0.98808 | 30.2 | 29.294 | NA | NA | 5 | Merewether 13233kV | 0.97
Blakehurst ZS | Summer | Asset condition - 11kV switchgear | -33.977 | 151.1155 | -33.977 | 151.1155 | ZN10991 | Zone Substation | 11742 | 94.63% | 31.6 | 31.6 | 31.6 | 31.6 | 31.6 | 30.939 | 30.939 | 30.939 | 30.939 | 30.939 | 25.7822 | 26.4738 | 27.2864 | 27.9613 | 28.7061 | 28.9587 | 29.7011 | 30.5395 | 31.2145 | 31.9592 | 25.2429 | 25.92 | 26.7156 | 27.3764 | 28.1056 | 28.353 | 29.0799 | 29.9007 | 30.5615 | 31.2907 | 11kV | 14.3396 | 15.0167 | 15.8123 | 16.4731 | 17.2023 | 4.8466 | 5.8639 | 6.6983 | 7.8479 | 9.0845 | Transfer all load to Kogarah and Hurstville North zone substations and decommission Blakehurst zone substation and associated 33kV gas cables | 24.6 | 0.123 | 30% | 10% | 2029-09-01 | 3 | 2.9372 | 0.84107 | 11.1363 | 10.9033 | NA | NA | 6 | Blakehurst 33/11kV | 0.97908
Fdr 769 Peakhurst STS - Blakehurst | Summer | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 769 | Sub-transmission line |  |  | 26.9 | 26.9 | 26.9 | 26.9 | 26.9 | 26.3373 | 26.3373 | 26.3373 | 26.3373 | 26.3373 | 26.2077 | 26.9309 | 27.7958 | 28.4955 | 29.2835 | NA | NA | NA | NA | NA | 25.6594 | 26.3675 | 27.2143 | 27.8995 | 28.6709 | NA | NA | NA | NA | NA | 33kV | 0 | 0.030237 | 0.87701 | 1.5622 | 2.3336 | 0.56696 | 0.84748 | 1.3559 | 2.0424 | 3.0495 | [9 empty] | 11.1363 | 10.9033 | NA | NA | 6 | Blakehurst 33/11kV | 0.97908
Fdr 770 Peakhurst STS - Blakehurst | Summer | Asset Condition - 33kV feeder | -33.9659 | 151.0626 | -33.977 | 151.1155 | Fdr 770 | Sub-transmission line |  |  | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.2394 | 26.2394 | 26.2394 | 26.2394 | 26.2394 | 26.2077 | 26.931 | 27.7958 | 28.4956 | 29.2836 | NA | NA | NA | NA | NA | 25.6595 | 26.3676 | 27.2144 | 27.8996 | 28.6711 | NA | NA | NA | NA | NA | 33kV | 0 | 0.12822 | 0.97501 | 1.6602 | 2.4317 | Combined with Fdr 769 Peakhurst STS - Blakehurst | [13 empty] | 11.1363 | 10.9033 | NA | NA | 6 | Blakehurst 33/11kV | 0.97908
`

## System Limitations TAPR - STS
System Limitations TAPR - STS
[97 empty] | 0 | 0 | 0 | 0 | 0 | 144540 | 264114 | 352152 | 440190 | 528228
Connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point (Latitude) | Constrained connection point (Longitude) | Annual energy of residential customers affected (MWh) | Peak demand of residential customers affected (MW) | Annual energy of industrial customers affected (MWh) | Peak demand of industrial customers affected (MW) | Annual energy of commercial customers affected (MWh) | Peak demand of commercial customers affected (MW) | Forecast P50 Max Demand on max demand day (MVA) & S24/25 or W25 | Forecast P50 Max Demand on max demand day (MVA) & S25/26 or W26 | Forecast P50 Max Demand on max demand day (MVA) & S26/27 or W27 | Forecast P50 Max Demand on max demand day (MVA) & S27/28 or W28 | Forecast P50 Max Demand on max demand day (MVA) & S28/29 or W29 | Forecast P50 Max Demand on max demand day (MVA) & S29/30 or W30 | Forecast P50 Max Demand on max demand day (MVA) & S30/31 or W31 | Forecast P50 Max Demand on max demand day (MVA) & S31/32 or W32 | Forecast P50 Max Demand on max demand day (MVA)& S32/33 or W33 | Forecast P50 Max Demand on max demand day (MVA)& S33/34 or W34 | Forecast P10 Max Demand on max demand day (MVA) S24/25 or W25 | Forecast P10 Max Demand on max demand day (MVA) S25/26 or W26 | Forecast P10 Max Demand on max demand day (MVA) S26/27 or W27 | Forecast P10 Max Demand on max demand day (MVA) S27/28 or W28 | Forecast P10 Max Demand on max demand day (MVA) S28/29 or W29 | Forecast P10 Max Demand on max demand day (MVA) S29/30 or W30 | Forecast P10 Max Demand on max demand day (MVA) S30/31 or W31 | Forecast P10 Max Demand on max demand day (MVA) S31/32 or W32 | Forecast P10 Max Demand on max demand day (MVA) S32/33 or W33 | Forecast P10 Max Demand on max demand day (MVA) S33/34 or W34 | Forecast P50 Max Demand on min demand day (MW) S24/25 or W25 | Forecast P50 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P50 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P50 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P50 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P50 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P50 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P50 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P50 Max Demand on min demand day (MW) S32/33 or W33 | Forecast P50 Max Demand on min demand day (MW) S33/34 or W34 | Forecast P10 Max Demand on min demand day (MW) S24/25 or W25 | Forecast P10 Max Demand on min demand day (MW) S25/26 or W26 | Forecast P10 Max Demand on min demand day (MW) S26/27 or W27 | Forecast P10 Max Demand on min demand day (MW) S27/28 or W28 | Forecast P10 Max Demand on min demand day (MW) S28/29 or W29 | Forecast P10 Max Demand on min demand day (MW) S29/30 or W30 | Forecast P10 Max Demand on min demand day (MW) S30/31 or W31 | Forecast P10 Max Demand on min demand day (MW) S31/32 or W32 | Forecast P10 Max Demand on min demand day (MW) S32/33 or W33 | Forecast P10 Max Demand on min demand day (MW) S33/34 or W34 | Voltage level (kV) | Maximum Load at risk per year (MVA) S24/25 or W25 | Maximum Load at risk per year (MVA) S25/26 or W26 | Maximum Load at risk per year (MVA) S26/27 or W27 | Maximum Load at risk per year (MVA) S27/28 or W28 | Maximum Load at risk per year (MVA) S28/29 or W29 | Maximum Load at risk per year (MVA) S29/30 or W30 | Maximum Load at risk per year (MVA) S30/31 or W31 | Maximum Load at risk per year (MVA) S31/32 or W32 | Maximum Load at risk per year (MVA) S32/33 or W33 | Maximum Load at risk per year (MVA) S33/34 or W34 | Maximum Load at risk per year (MW) S24/25 or W25 | Maximum Load at risk per year (MW) S25/26 or W26 | Maximum Load at risk per year (MW) S26/27 or W27 | Maximum Load at risk per year (MW) S27/28 or W28 | Maximum Load at risk per year (MW) S28/29 or W29 | Maximum Load at risk per year (MW) S29/30 or W30 | Maximum Load at risk per year (MW) S30/31 or W31 | Maximum Load at risk per year (MW) S31/32 or W32 | Maximum Load at risk per year (MW) S32/33 or W33 | Maximum Load at risk per year (MW) S33/34 or W34 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Load transfer capacity (MVA) | Historic connection point rating (MVA) S21/22 or W22 | Historic connection point rating (MVA) S22/23 or W23 | Historic connection point rating (MVA) S23/24 or W24 | Limitation asset | Unplanned outages | Maximum fault level (MVA) | Annual economic cost of constraint ($constant) S24/25 or W25 | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | Annual economic cost of constraint ($constant) S33/34 or W34 | VCR ($/MWh) | Annual EUE (MWh) S24/25 or W25 | Annual EUE (MWh) S25/26 or W26 | Annual EUE (MWh) S26/27 or W27 | Annual EUE (MWh) S27/28 or W28 | Annual EUE (MWh) S28/29 or W29 | Annual EUE (MWh) S29/30 or W30 | Annual EUE (MWh) S30/31 or W31 | Annual EUE (MWh) S31/32 or W32 | Annual EUE (MWh) S32/33 or W33 | Annual EUE (MWh) S33/34 or W34 | Project Index for additional data%
Wallumatta STS (Macquarie Park) | Load growth - Substation capacity and connection points |  | -33.7872 | 151.1323 | N/A | N/A | N/A | N/A | N/A | N/A | 96.05 | 156.4 | 233.75 | 312.8 | 366.35 | 433.5 | 484.5 | 536.35 | 553.35 | 581.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 132 | 0 | 45 | 110 | 181 | 219 | 278 | 321 | 379 | 395 | 416 | 0 | 45 | 110 | 181 | 219 | 278 | 321 | 379 | 395 | 416 | Establish New Wallumatta STS | 162.3 | 0.143 | +/-30% | 2028-12-01 | NA | 5.549 | 0 | 0 | 0 | 0 | Transformer and 33kV switchgear | N/A | N/A | 0 | 0.01 | 10.96 | 3048.83 | 10250976.1 | 5631388194.86 | 24200369623.76 | 53156379670.41 | 64027190043.42 | 82683113520.71 | 52024 | 0 | 1.9222e-07 | 0.00021067 | 0.058604 | 197.0432 | 108245.9671 | 465177.0264 | 1021766.4861 | 1230724.0897 | 1589326.3402
Mascot East | Load growth - Substation capacity and connection points |  | -33.914409 | 151.1906 | [6 empty] | 0 | 30 | 60 | 120 | 140 | 140 | 140 | 140 | 140 | 140 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [20 empty] | 132 | 0 | 30 | 60 | 120 | 140 | 140 | 140 | 140 | 140 | 140 | 0 | 29.4 | 58.8 | 117.6 | 137.2 | 137.2 | 137.2 | 137.2 | 137.2 | 137.2 | Establish New Mascot East switching station | 31.3 | 0.1565 | +/-30% | 2029-12-01 | N/A | 1.0701 | 0 | 0 | 0 | 0 | 132kV feeder | N/A | N/A | 0 | 13398469056 | 26796938112 | 53593876224 | 62526188928 | 62526188928 | 62526188928 | 62526188928 | 62526188928 | 62526188928 | 52024 | 0 | 257544 | 515088 | 1030176 | 1201872 | 1201872 | 1201872 | 1201872 | 1201872 | 1201872

## System Limitations TAPR - Lines
System Limitations TAPR - Lines
Transmission line ID | Constraint primary driver | Location of constraint (start) Latitude | Location of constraint (start) Longitude | Location of constraint (end) Latitude | Location of constraint (end) Longitude | Asset rating (MVA) S24/25 or W25 | Asset rating (MVA) S25/26 or W26 | Asset rating (MVA) S26/27 or W27 | Asset rating (MVA) S27/28 or W28 | Asset rating (MVA) S28/29 or W29 | Asset rating (MVA) S29/30 or W30 | Asset rating (MVA) S30/31 or W31 | Asset rating (MVA) S31/32 or W32 | Asset rating (MVA) S32/33 or W33 | Asset rating (MVA) S33/34 or W34 | Forecast Demand P50 (MVA) S24/25 or W25 | Forecast Demand P50 (MVA) S25/26 or W26 | Forecast Demand P50 (MVA) S26/27 or W27 | Forecast Demand P50 (MVA) S27/28 or W28 | Forecast Demand P50 (MVA) S28/29 or W29 | Forecast Demand P50 (MVA) S29/30 or W30 | Forecast Demand P50 (MVA) S30/31 or W31 | Forecast Demand P50 (MVA) S31/32 or W32 | Forecast Demand P50 (MVA) S32/33 or W33 | Forecast Demand P50 (MVA) S33/34 or W34 | Forecast Demand P10 (MVA) S24/25 or W25 | Forecast Demand P10 (MVA) S25/26 or W26 | Forecast Demand P10 (MVA) S26/27 or W27 | Forecast Demand P10 (MVA) S27/28 or W28 | Forecast Demand P10 (MVA) S28/29 or W29 | Forecast Demand P10 (MVA) S29/30 or W30 | Forecast Demand P10 (MVA) S30/31 or W31 | Forecast Demand P10 (MVA) S31/32 or W32 | Forecast Demand P10 (MVA) S32/33 or W33 | Forecast Demand P10 (MVA) S33/34 or W34 | Voltage level | Maximum Load at risk per year (MVA)* S24/25 or W25 | Maximum Load at risk per year (MVA)* S25/26 or W26 | Maximum Load at risk per year (MVA)* S26/27 or W27 | Maximum Load at risk per year (MVA)* S27/28 or W28 | Maximum Load at risk per year (MVA)* S28/29 or W29 | Maximum Load at risk per year (MVA)* S29/30 or W30 | Maximum Load at risk per year (MVA)* S30/31 or W31 | Maximum Load at risk per year (MVA)* S31/32 or W32 | Maximum Load at risk per year (MVA)* S32/33 or W33 | Maximum Load at risk per year (MVA)* S33/34 or W34 | Maximum Load at risk per year (MW)* S24/25 or W25 | Maximum Load at risk per year (MW)* S25/26 or W26 | Maximum Load at risk per year (MW)* S26/27 or W27 | Maximum Load at risk per year (MW)* S27/28 or W28 | Maximum Load at risk per year (MW)* S28/29 or W29 | Maximum Load at risk per year (MW)* S29/30 or W30 | Maximum Load at risk per year (MW)* S30/31 or W31 | Maximum Load at risk per year (MW)* S31/32 or W32 | Maximum Load at risk per year (MW)* S32/33 or W33 | Maximum Load at risk per year (MW)* S33/34 or W34 | Energy at risk (MWh) S24/25 or W25 | Energy at risk (MWh) S25/26 or W26 | Energy at risk (MWh) S26/27 or W27 | Energy at risk (MWh) S27/28 or W28 | Energy at risk (MWh) S28/29 or W29 | Energy at risk (MWh) S29/30 or W30 | Energy at risk (MWh) S30/31 or W31 | Energy at risk (MWh) S31/32 or W32 | Energy at risk (MWh) S32/33 or W33 | Energy at risk (MWh) S33/34 or W34 | Preferred investment - Description | Preferred investment - Capital cost ($M REAL) | Preferred investment - Annual operating cost ($M REAL) | Preferred investment - Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MVA) | Annual Deferral Value ($M REAL) | Historic line rating (MVA) S21/22 or W22 | Historic line rating (MVA) S22/23 or W23 | Historic line rating (MVA) S23/24 or W24 | Annual economic cost of constraint ($constant) S24/25 or W25 | Annual economic cost of constraint ($constant) S25/26 or W26 | Annual economic cost of constraint ($constant) S26/27 or W27 | Annual economic cost of constraint ($constant) S27/28 or W28 | Annual economic cost of constraint ($constant) S28/29 or W29 | Annual economic cost of constraint ($constant) S29/30 or W30 | Annual economic cost of constraint ($constant) S30/31 or W31 | Annual economic cost of constraint ($constant) S31/32 or W32 | Annual economic cost of constraint ($constant) S32/33 or W33 | Annual economic cost of constraint ($constant) S33/34 or W34 | VCR ($/MWh) | Annual costraint duration (hours)# | Constraint duration on peak demand day (hours)# | Project Index for interval data
Fdr 91A - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 37.0034 | 36.2307 | 38.3886 | 40.0207 | 39.358 | 38.9852 | 41.5761 | 61.6405 | 59.6876 | 59.0319 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.9196 | 26.0147 | 29.8091 | 33.7622 | 38.2551 | 43.1272 | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | 20.3 | 0.0406 | 30% | 2029-09-01 | NA | 0.69405 | 97.17 | 97.17 | 97.17 | 122021.6819 | 128016.9194 | 134472.0949 | 141413.4159 | 1634942.1081 | 1843618.224 | 2098210.5359 | 2363691.2825 | 2664834.1555 | 2991203.2166 | 64837.627 | 0.67624 | 0.0018527 | 1
Fdr 91B - Beaconsfield BSP to St Peters ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9068 | 151.1834 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 97.17 | 37.7294 | 37.0261 | 39.2098 | 40.8574 | 40.1307 | 39.7866 | 42.4045 | 62.8116 | 60.8016 | 60.1559 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [9 empty] | Replace with new 132kV feeder from Beaconsfield BSP to St Peters ZS | [6 empty] | 97.17 | 97.17 | 97.17 | Combined with Fdr 91A - Beaconsfield BSP to St Peters ZS | [12 empty] | 1
Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 50.6302 | 51.3373 | 53.544 | 55.2144 | 54.5107 | 54.502 | 57.3086 | 78.7114 | 76.9267 | 76.521 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0048769 | 0.0071667 | 0.011189 | 0.015558 | 0.02057 | 0.028271 | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91X/1 | 1.03 | - | 30% | 2028-09-01 | 5 | 0.035215 | 99.45 | 99.45 | 99.45 | 134426.5868 | 139684.8075 | 145383.6579 | 151550.7011 | 158512.5449 | 165835.9371 | 173816.7079 | 182408.0775 | 191686.3817 | 201754.5619 | 57181 | 0.0018037 | 4.9415e-06 | 2
Fdr 91Y/1 - Beaconsfield BSP to Marrickville ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9118 | 151.1624 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 99.45 | 50.5881 | 51.2941 | 53.5168 | 55.1628 | 54.4721 | 54.4453 | 57.2537 | 78.6751 | 76.8714 | 76.4677 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | [9 empty] | Re-arrange connections at Marrickville ZS to allow retirement of 132kV feeder 91Y/1 | [6 empty] | 99.45 | 99.45 | 99.45 | Combined with Fdr 91X/1 - Beaconsfield BSP to Marrickville ZS | [12 empty] | 2
Fdr 91X/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 73.1714 | 75.6644 | 77.8212 | 79.0923 | 78.053 | 79.3579 | 79.8986 | 102.6444 | 99.2664 | 99.9079 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 3.2 | - | 30% | 2028-09-01 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 100.6 | 100.6 | 100.6 | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [12 empty] | 3
Fdr 91Y/2 - Chullora STSS to Marrickville ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9118 | 151.1624 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 72.0761 | 72.6436 | 75.1334 | 77.1103 | 76.6815 | 77.3483 | 80.6744 | 103.2153 | 101.5587 | 101.7929 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [6 empty] | 100.6 | 100.6 | 100.6 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 3
Fdr 92C - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 69.4516 | 72.0483 | 74.0728 | 75.2368 | 74.211 | 75.4587 | 75.852 | 97.5346 | 94.2649 | 94.8708 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 3.5 | - | 30% | 2028-09-01 |  |  | 104.03 | 104.03 | 104.03 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 4
Fdr 92X - Chullora STSS to St Peters ZS | Asset condition - 132kV feeder | -33.8789 | 151.0658 | -33.9068 | 151.1834 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 104.03 | 70.3829 | 70.9455 | 73.3635 | 75.2674 | 74.9167 | 75.4858 | 78.8168 | 100.4285 | 98.9906 | 99.1597 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | [6 empty] | 104.03 | 104.03 | 104.03 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 4
Fdr 90T/1 - Haymarket BSP to Green Square ZS | Asset condition - 132kV feeder | -33.8815 | 151.2023 | -33.9123 | 151.1945 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 221.77 | 134.4841 | 135.5734 | 134.8416 | 134.4388 | 135.5271 | 138.9999 | 142.8904 | 152.3085 | 155.0081 | 157.3863 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 6 | - | 30% | 1934-06-01 |  |  | 221.77 | 221.77 | 221.77 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 5
Fdr 9S2 - Beaconsfield BSP to Haymarket BSP | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.8815 | 151.2023 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 121.6312 | 123.0145 | 123.6801 | 124.4455 | 126.0804 | 129.2188 | 132.4865 | 140.5347 | 142.8143 | 144.9557 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [9 empty] | Refer to RIT-T for joint Transgrid and Ausgrid project Powering Sydney's Future | 1.13 | - | 30% | 1934-06-01 |  |  | 225.2 | 225.2 | 225.2 | Combined with Fdr 91X/2 - Chullora STSS to Marrickville ZS | [12 empty] | 5
Fdr 9FF - Beaconsfield BSP to Bunnerong North STS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9695 | 151.2289 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 195.48 | 160.3149 | 167.2897 | 166.5724 | 160.4107 | 154.5815 | 155.747 | 156.0963 | 189.8952 | 182.0725 | 182.4379 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.755 | 71.3737 | 118.3525 | 126.4285 | 135.3407 | 145.1642 | 156.0134 | 167.9205 | Replace oil cable with new 132kV feeder from Beaconsfield BSP to Mill Pond Rd | 23.5 | 0.047 | 30% | 2029-12-01 | N/A | 0.80346 | 195.48 | 195.48 | 195.48 | 106629.8456 | 109456.4666 | 2440947.0685 | 3829238.8863 | 6277091.2993 | 6701411.2933 | 7169599.7244 | 7685594.5161 | 8255374.6113 | 8880617.6462 | 52024 | 0.98645 | 0.0027026 | 6
Fdr 9SE - Beaconsfield BSP to Green Square ZS | Asset condition - 132kV feeder | -33.915 | 151.1872 | -33.9123 | 151.1945 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 120.3519 | 127.8384 | 150.8695 | 172.5796 | 186.804 | 192.6364 | 194.5326 | 210.9708 | 211.96 | 217.2677 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8801 | 4.0168 | 4.358 | 4.6988 | 5.1275 | 5.6326 | 6.2115 | 6.7697 | 7.3413 | 7.9218 | Replace with new 132kV feeder from Beaconsfield BSP to Green Square ZS | 6.6 | 0.0132 | 30% | 1934-06-01 | 2 | 0.22565 | 225.2 | 225.2 | 225.2 | 210244.9535 | 286123.269 | 309020.013 | 331918.0178 | 360689.7294 | 394576.813 | 433400.9544 | 470879.7353 | 509285.8103 | 548309.9218 | 66619 | 0.22368 | 0.00061283 | 7
Fdr 270 - Kingsford ZS to Maroubra ZS | Asset condition - 132kV feeder | -33.927248 | 151.23 | -33.9422 | 151.238 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 225.2 | 93.043 | 103.6714 | 105.0163 | 97.5829 | 89.516 | 89.8502 | 88.0489 | 118.0716 | 109.2011 | 108.0718 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 132kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0308 | 0.94809 | 0.91345 | 0.90506 | 0.91391 | 0.96595 | 1.0593 | 1.1234 | 1.1551 | 1.1819 | Replace with two new 132kV feeders (Bunnerong STSS - Kingsford ZS, Maroubra ZS - Clovelly ZS) and decommission 132kV feeder 262 | 6.5 | 0.013 | 30% | 1934-06-01 | N/A | 0.22223 | 225.2 | 225.2 | 225.2 | 207552.658 | 207472.1855 | 210810.1328 | 216247.8421 | 223278.3065 | 233502.1214 | 246858.2578 | 259010.3062 | 269843.0911 | 281034.0048 | 61794 | 0.22668 | 0.00062104 | 8
*Maximum load at risk is provided for credible contingencies and only assumes committed projects
#Constraint duration provided for year of proposed timing of preferred investment