## Tx calculator
EGN 422: Transformer Noise Calculator
Version 4 - 11 December 2023 | [26 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
[19 empty] | Equations can be found here | [7 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
Transformer Noise | [18 empty] | https://noisetools.net/noisecalculator | [7 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
| Transformer |  |  |  |  | STEP A | [20 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
[19 empty] | Jan 2022 revision | [7 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
| Transformer Sound Power Level | 68 | dB | [14 empty] | 1 | CW2235421 | ETEL | E kiosk | 750 | ETEL E kiosk 750 kVA | 60 | 57 |  | Use these transformers until the ETEL transformers on contract CW2235421 is approved
[18 empty] | 2 |  | ETEL | City/Suburban Chamber | 1500 | ETEL City/Suburban Chamber 1500 kVA | 68 | 58 |  | Use these transformers until the ETEL transformers on contract CW2235421 is approved
| Distance to nearest receiver | 1 | m | [14 empty] | 3 |  | ETEL | City/Suburban Chamber | 1000 | ETEL City/Suburban Chamber 1000 kVA | 66 | 59 |  | Use these transformers until the ETEL transformers on contract CW2235421 is approved
[18 empty] | 4 |  | ETEL | City/Suburban Chamber | 750 | ETEL City/Suburban Chamber 750 kVA | 65 | 55
| Surface between kiosk and receiver |  |  |  | STEP B | [12 empty] | 5 | EA7578/05 | Schneider | City/Suburban Chamber | 1500 | Schneider City/Suburban Chamber 1500 kVA | 68 | 56.5 |  | Dropdown 1 | 2
[18 empty] | 6 |  | Schneider | City/Suburban Chamber | 1000 | Schneider City/Suburban Chamber 1000 kVA | 66 | 65.3 |  | Dropdown 2 | 2 | Soft - grass/dirt
| Is kiosk in front of a masonary wall | [16 empty] | 7 |  | Schneider | City/Suburban Chamber Dual Voltage | 1000 | Schneider City/Suburban Chamber Dual Voltage 1000 kVA | 65 | 63 |  | Dropdown 3 | 2 | Hard - concrete/ashphalt
| (ie additional noise reflects towards receiver) | [16 empty] | 8 |  | Wilson | City/Suburban Chamber | 750 | Wilson City/Suburban Chamber 750 kVA | 65 | 45 |  |  |  | Yes
[18 empty] | 9 | CW2227437 | Wilson | Vault/CBD Underground | 1000 | Wilson Vault/CBD Underground 1000 kVA | 58 | 52.4 |  |  |  | No
[18 empty] | 10 |  | Wilson | Vault/CBD Underground | 750 | Wilson Vault/CBD Underground 750 kVA | 56 | 53
| Reduction due to distance / surface | -8 | dB | [14 empty] | 11 | CW2240523 | Tyree | Pole Top 3ph | 400 | Tyree Pole Top 3ph 400 kVA | 56 | 52
[18 empty] | 12 |  | Tyree | Pole Top 3ph | 200 | Tyree Pole Top 3ph 200 kVA | 56 | 55
| Noise at reciever (no barrier / reflection) | 60 | dB (Sound Pressure Level) | [14 empty] | 13 |  | Tyree | Pole Top 3ph | 100 | Tyree Pole Top 3ph 100 kVA | 56 | 51.4
[18 empty] | 14 |  | Tyree | Pole Top 3ph | 63 | Tyree Pole Top 3ph 63 kVA | 56 | 49.5
[18 empty] | 15 |  | Tyree | Pole Top 3ph | 25 | Tyree Pole Top 3ph 25 kVA | 56 | 50
[8 empty] | 6 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16 | 16 |  | Tyree | Pole Top 1ph | 63 | Tyree Pole Top 1ph 63 kVA | 56 | 52
Barrier | [7 empty] | 7 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16 | 17 |  | Tyree | Pole Top 1ph | 25 | Tyree Pole Top 1ph 25 kVA | 56 | 44
[8 empty] | 8 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16 | 18 |  | Tyree | Pole Top 1ph | 16 | Tyree Pole Top 1ph 16 kVA | 56 | 45
| Is there a solid barrier between the transformer (Tx) and the receiver (residence)? |  |  | STEP C | [13 empty] | 19 | AG3530/11 | ABB Hitachi | Dry type | 1500 | ABB Hitachi Dry type 1500 kVA | 68 | 65
[18 empty] | 20 | CW2244809 | Tyree | L kiosk | 1000 | Tyree L kiosk 1000 kVA | 62 | 61.8
| If yes, enter dimensions in metres below: | [16 empty] | 21 |  | Tyree | L kiosk | 800 | Tyree L kiosk 800 kVA | 60 | 52
[18 empty] | 22 |  | Tyree | L kiosk | 600 | Tyree L kiosk 600 kVA | 59 | 58.4
| a | 5 | [15 empty] | 23 |  | Tyree | L kiosk | 400 | Tyree L kiosk 400 kVA | 57 | 56.7
| b | 6.7 |  | STEP D (if required) | [13 empty] | 24 | CW2245875 | Schneider | K kiosk | 1500 | Schneider K kiosk 1500 kVA | 65 | 64.6
| c | 9 | [15 empty] | 25 |  | Schneider | L kiosk | 1000 | Schneider L kiosk 1000 kVA | 62 | 59.3
| d | 3.9 | [15 empty] | 26 |  | Schneider | L kiosk | 800 | Schneider L kiosk 800 kVA | 60 | 50
| e | 6.5 | [15 empty] | 27 |  | Schneider | L kiosk | 600 | Schneider L kiosk 600 kVA | 59 | 55.7
[18 empty] | 28 |  | Schneider | L kiosk | 400 | Schneider L kiosk 400 kVA | 57 | 55.8
| a+b-c | 2.7 | [15 empty] | 29
| d+e-c | 1.4 | [15 empty] | 30
* prototype production/ testing in progress
| Reduction from the barrier | -9 | dB
2
Yes
No
Background level | [18 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Type of area | [5 empty] | STEP E | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 1 | 0 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Background Noise | 35 | dB | [14 empty] | 2 | 0 | 9 | 11 | 12 | 13 | 13.5 | 14 | 14 | 14
[18 empty] | 3 | 0 | 10 | 12 | 13 | 14 | 14.5 | 15 | 15 | 15
[18 empty] | 4 | 0 | 10 | 12 | 14 | 14.5 | 15 | 15.5 | 16 | 16
[18 empty] | 5 | 0 | 10 | 12 | 14 | 15 | 15.5 | 16 | 16 | 16
Are control measures required?
| Total Predicted Noise | 60 | dB (Sound Pressure Level) | [14 empty] | 2 | 0: Description of Neighbourhood; 1: Average Background Level, LA90, T dB(A)
| Allowable criteria | 35 | dB | [14 empty] | 1 | 0: Negligible transportation; 1: 30
[18 empty] | 2 | 0: Low density transportation; 1: 35
| Acceptable? | You will need to consider further mitigation measures |  |  | ANSWER | [12 empty] | 3 | 0: Medium density transportation or some commerce or industry; 1: 40
[18 empty] | 5 | 0: Very dense transportation or in commercial districts or bordering industrial districts; 1: 50
[18 empty] | 6 | 0: Extremely dense transportation or within predominantly industrial districts; 1: 55
INSTRUCTIONS Use the transformer noise calculator to predict the noise level from a transformer installation and determine if it meets the allowable criteria. If the predicted noise does not meet the allowable criteria, you will need to consider further mitigation measures. STEP A: Indicate the type of transformer. STEP B: Indicate the distance to the nearest receiver, type of surface between kiosk and receiver and whether the kiosk is in front of a masonary wall (ie reflection effect towards receiver). STEP C: Indicate if there is a solid barrier between the transformer and the receiver. STEP D: If there is a solid barrier, determine the distances in metres using the diagram as a guide. The reduction from the barrier will be calculated. STEP E: Indicate the type of area the transformer is being installed in to determine the background noise. The total predicted noise and allowable criteria will be calculated. Sound Power Level is a measure of the acoustic energy emitted from a source (independent of distance). Sound pressure is what you hear.

## Generic calculator
Generic Calculator
Version 4 - 11 December 2023 | [30 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
[23 empty] | Equations can be found here | [7 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
Noise source | [22 empty] | https://noisetools.net/noisecalculator | [7 empty] | Not YET used in calculator. Wait until contract CW2235421 is approved
| Known sound pressure | 56 | dB
STEP A
| … at a distance of | 5 | m
| Calculated Sound Power Level | 77.9794 | dB | [27 empty] | Use these transformers until the ETEL transformers on contract CW2235421 is approved
Use these transformers until the ETEL transformers on contract CW2235421 is approved
| Distance to nearest receiver | 10 | m | [27 empty] | Use these transformers until the ETEL transformers on contract CW2235421 is approved
| Surface between kiosk and receiver |  |  |  |  | STEP B | [24 empty] | Dropdown 1 | 2
[31 empty] | Dropdown 2 | 2 | Soft - grass/dirt
| Is source in front of a masonary wall | [29 empty] | Dropdown 3 | 2 | Hard - concrete/ashphalt
| (ie additional noise reflects towards receiver) | [31 empty] | Yes
No
| Reduction due to distance / surface | -28 | dB
| Noise at reciever (no barrier / reflection) | 49.9794 | dB (Sound Pressure Level)
[11 empty] | 6 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16
Barrier | [10 empty] | 7 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16
[11 empty] | 8 | 0 | 10 | 12 | 14 | 15 | 16 | 16 | 16 | 16
| Is there a solid barrier between the source and the receiver (residence)? |  |  | STEP C
If yes, enter dimensions in metres below:
| a | 4.2
| b | 7.6 |  | STEP D (if required)
| c | 10
| d | 5.8
| e | 8.6 |  |  |  |  | The following can be used to calculate a, b, c, d and e
[7 empty] | Source height |  | 2
| a+b-c | 1.8 |  |  |  |  | Receiver height |  | 2 | a= | [10 empty] | 4.2426
| d+e-c | 4.4 |  |  |  |  | Wall height |  | 5 | b= | [10 empty] | 7.6158
[7 empty] | Wall length |  | 10 | c= | [10 empty] | 10
| Reduction from the barrier | -10 | dB |  |  |  | Dist - source to receiver |  | 10 | d= | [10 empty] | 5.831
[7 empty] | Dist - source to barrier |  | 3 | e= | [10 empty] | 8.6023 | 2
Yes
No
Background level | [22 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
| Type of area | [6 empty] | STEP E | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 1 | 0 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Background Noise | 35 | dB | [18 empty] | 2 | 0 | 9 | 11 | 12 | 13 | 13.5 | 14 | 14 | 14
[22 empty] | 3 | 0 | 10 | 12 | 13 | 14 | 14.5 | 15 | 15 | 15
[22 empty] | 4 | 0 | 10 | 12 | 14 | 14.5 | 15 | 15.5 | 16 | 16
[22 empty] | 5 | 0 | 10 | 12 | 14 | 15 | 15.5 | 16 | 16 | 16
Modifying factors
| Total noise penalty | 0 | dB |  |  |  |  | STEP F
(refer to table on the right)
Are control measures required?
| Total Predicted Noise | 49.9794 | dB (Sound Pressure Level) | [18 empty] | 2 | 0: Description of Neighbourhood; 1: Average Background Level, LA90, T dB(A); 2: 0
| Allowable criteria | 35 | dB | [18 empty] | 1 | 0: Negligible transportation; 1: 30; 2: 2
[22 empty] | 2 | 0: Low density transportation; 1: 35; 2: 5
| Acceptable? | You will need to consider further mitigation measures |  |  | ANSWER | [16 empty] | 3 | 0: Medium density transportation or some commerce or industry; 1: 40; 2: 7
[22 empty] | 4 | 0: Dense transportation or some commerce or industry; 1: 45; 2: 10
INSTRUCTIONS Use the generic noise calculator to predict the noise level from a noise source and determine if it meets the allowable criteria. If the predicted noise does not meet the allowable criteria, you will need to consider further mitigation measures. STEP A: Enter the known sound pressure at a given distance. STEP B: Indicate the distance to the nearest receiver, type of surface between kiosk and receiver and whether the source is in front of a masonary wall (ie reflection effect towards receiver). STEP C: Indicate if there is a solid barrier between the transformer and the receiver. STEP D: If there is a solid barrier, determine the distances in metres using the diagram as a guide. The reduction from the barrier will be calculated. STEP E: Indicate the type of area the source is being installed in to determine the background noise. The total predicted noise and allowable criteria will be calculated. STEP F: Select appropriate modifying factor if applicable. Sound Power Level is a measure of the acoustic energy emitted from a source (independent of distance). Sound pressure is what you hear.

## Other
Sound Attenuation Calculator |  |  |  | Sound Power vs Sound Pressure |  |  | Adding noise sources
Dist A | 1 | m |  | Sound pressure | 75 | dB - changes with distance | Source 1 | 1 | dB
Noise at A | 75 | dB |  | Distance to centre of source | 1 | m - hemishpere must enclose source | Source 2 | 1 | dB
Dist B | 10 | m |  | Measurement surface area | 6.2832 | m^3 - hemisphere | Sound power | 4.0103
Noise at B | 55 | dB |  | Sound power | 82.9818 | dB - independent of distance
X |  | X | X
Source |  | A | B | Sound power | 83 | dB - independent of distance
|  |  |  | Distance to centre of source | 10 | m - hemishpere must enclose source
|  |  |  | Measurement surface area | 628.3185 | m^3 - hemisphere
|  |  |  | Sound pressure | 55.0182 | dB - changes with distance